## NW Quad (thru 5-23) 8", 10",12"
MI Owosso/OHM Project
Segments with incomplete or no inspections through May 23
Northwest Quadrant (8", 10", 12")
Date | U/S MH | D/S MH | Segment ID | Map Page | Pipe Size | Map Length | Inspected Length | Comments
2016-05-16 | SNM-1401-013 | SNM-1401-012 | SGM-1401-013 | C1 | 8 | 304 | 252 | 252 feet on my initial lunch and the reversal had to be nulled do to surcharge in the line at SMN-1401-013
2016-05-16 | SNM-1401-030 | SNM-1401-029 | SGM-1401-032 | C2 | 8 | 47 | 20 | False start pipe condition on the initial run of 2 feet and a run of 18 feet on the reversal.
2016-05-18 | SNM-1401-021 | SNM-1401-038 | SGM-1401-040 | C2 | 8 | 86 | 77 | Pipe condition on the initial run of 41 feet as well as on the reversal run of 36 feet,
2016-05-18 | SNM-1401-022 | SNM-1401-021 | SGM-1401-022 | C2 | 8 | 228 | 8 | False start pipe condition on the first run of 5 feet as well as on the reversal run of 3 feet
2016-05-18 | SNM-1401-055 | SNM-1401-042 | SGM-1401-058 | C2 | 8 | 209 | 89 | pipe condition on the initial run of 89 feet. The reversal was nulled SNM-1401-042 full of debris
2016-05-19 | SNM-1401-023 | SNM-1401-022 | SGM-1401-023 | C2 | 8 | 213 | 68 | Pipe condition on the first run of 61 feet as well as on the reversal of 7 feet.
2016-05-19 | SNM-1401-024 | SNM-1401-023 | SGM-1401-024 | C2 | 8 | 113 | 19 | Pipe condition on the initial run of 12 feet as well as on the reversal run of 7 feet
2016-05-19 | SNM-1401-025 | SNM-1401-023 | SGM-1401-025 | C2 | 8 | 175 | 68 | 68 feet on the first run but the reversal was nulled because of bricks piled up infront of the mouth of the pipe at SNM-1401-025
2016-05-19 | SNM-1401-026 | SNM-1401-024 | SGM-1401-027 | C2 | 8 | 152 | 13 | Roll max pipe condition on first run of 4 feet and Pipe condition on the reversal run of 9 feet.
2016-05-19 | SNM-1401-027 | SNM-1401-026 | SGM-1401-028 | C2 | 8 | 188 | 0 | Robot got stuck in the line and shut down. Didn't run reversal
2016-05-19 | SNM-1401-028 | SNM-1401-027 | SGM-1401-029 | C2 | 8 | 32 | 28 | Pipe condition on the initial run of 24 feet as well as on the reversal of 4 feet.
2016-05-21 | SNM-1304-048 | SNM-1304-049 | SGM-1304-053 | C2 | 8 | 326 | 42 | 42 feet on the first run and had to null the reversal because I couldn't get in the pipe at SNM-1304-048.
2016-05-21 | SNM-1304-049 | SNM-1304-045 | SGM-1304-052 | C2 | 8 | 285 | 202 | Pipe condition on the initial run of44 feet as well as on the reversal of 158 feet.
2016-05-21 | SNM-1304-050 | SNM-1304-049 | SGM-1304-055 | C2 | 8 | 298 | 26 | Pipe conditions on the initial run of 21 feet as well as the reversal of 5 feet
2016-05-21 | SNM-1304-051 | SNM-1304-050 | SGM-1304-058 | C2 | 8 | 219 | 59 | False start pipe condition on the initial run of 5 feet. Ran the reversal of 54 feet on 5/22/16 with a pipe condition result
2016-05-21 | SNM-1304-052 | SNM-1304-048 | SGM-1304-054 | C2 | 8 | 297 | ? | robot got stuck in t he line and had to be jetted, I don't know the outcome of the run.
2016-05-21 | SNM-1304-053 | SNM-1304-050 | SGM-1304-056 | C2 | 8 | 320 | 39 | Pipe condition on the first run of 10 feet as well as on the reversal of 29 feet.
2016-05-21 | SNM-1304-054 | SNM-1304-053 | SGM-1304-057 | C2 | 8 | 311 | 27 | Pipe condition on the initial run of 22 feet as well as on the reversal run of 5 feet.
2016-05-21 | SNM-1401-083 | SNM-1401-082 | SGM-1401-087 | C2 | 8 | 254 | 41 | Pipe condition on the first run of 41 feet and had to null the reversal because I can't open manhole SNM-1401-083
2016-05-21 | SNM-1401-084 | SNM-1401-083 | SGM-1401-088 | C2 | 8 | 245 | 0 | CNL SNM-1401-084; couldn't open the manhole at SNM-1401-83.
2016-05-22 | SNM-1304-079 | SNM-1304-051 | SGM-1304-059 | C2 | 8 | 154 | 4 | Pipe condition on initial run of 4 feet, nulled the reversal because the manhole won't open at SNM-1304-079
2016-05-22 | SNM-1401-081 | SNM-1401-080 | SGM-1401-085 | C2 | 8 | 277 | 192 | Pipe condition on initial run of 192 feet but got stuck in the line on the reversal run.
2016-05-22 | SNM-1401-082 | SNM-1401-081 | SGM-1401-086 | C2 | 8 | 311 | 150 | Pipe condition on the first run of 71 feet as well as on the reversal run of 79 feet.
2016-05-23 | SNM-1304-036 | SNM-1304-035 | SGM-1304-040 | C2 | 8 | 207 | 165 | Pipe condition on initial run of 76 feet as well as on the reversal run of 89 feet
2016-05-23 | SNM-1304-037 | SNM-1304-035 | SGM-1304-041 | C2 | 8 | 134 | 127 | Pipe condition on the first run of 127 feet and a nulled reversal due to heavy debris in line
2016-05-23 | SNM-1401-079 | SNM-1401-078 | SGM-1401-083 | C2 | 8 | 289 | 206 | Pipe condition on yhe first run of 206 feet but nulled reversal due to not being able to open SNM-1401-078
2016-05-17 | SNM-1401-017 | SNM-1401-050 | SGM-1401-053 | D1 | 8 | 223 | 194 | Pipe condition on initial run of 19 feet as well as on the reversal run of 175 feet
2016-05-17 | SNM-1401-018 | SNM-1401-017 | SGM-1401-018 | D1 | 8 | 318 | 67 | Pipe condition on the initial run of 38 feet as well as on the reversal run of 29 feet.
2016-05-17 | SNM-1401-019 | SNM-1401-018 | SGM-1401-019 | D1 | 8 | 464 | 16 | 16 feet on my initial run but had to null thew reversal because the pipes are fused together at SNM-1401-019. There's no access
2016-05-17 | SNM-1401-045 | SNM-1401-044 | SGM-1401-047 | D1 | 8 | 77 | 2 | false start pipe condition on the initial run of2 feet. Nulled the reversal due to SMN-1401-044 being compacted with cement at the mouth of the pipe.
2016-05-17 | SNM-1401-046 | SNM-1401-045 | SGM-1401-048 | D1 | 8 | 141 | 66 | False start pipe condition on the initial run of 0 feet, flagged image looks like a reduction. 66 feet on the reversal run also resulting in a pipe condition.
2016-05-17 | SNM-1401-047 | SNM-1401-046 | SGM-1401-049 | D1 | 8 | 177 | 17 | Pipe condition on the first run of 6 feet as well as on the reversal run of 11 feet.
2016-05-17 | SNM-1401-049 | SNM-1401-048 | SGM-1401-051 | D1 | 8 | 63 | 4 | False start Pipe condition on my first run of 4 feet Flagged the photo looks to be a reduction. Nulled the reversal. SNM-1401-049 cemented shut
2016-05-17 | SNM-1401-050 | SNM-1401-049 | SGM-1401-052 | D1 | 8 | 241 | 25 | Pipe condition on my initial run of 25 feet. Nulled the reversal, SNM-1401-049 is cemented closed.
2016-05-18 | SNM-1401-039 | SNM-1401-038 | SGM-1401-041 | D2 | 8 | 253 | 237 | Pipe condition in the first run of 229 feet as well as on the reversal run of 8 feet.
2016-05-18 | SNM-1401-040 | SNM-1401-039 | SGM-1401-042 | D2 | 8 | 209 | 9 | Pipe condition on the initial run of 9 feet. Robot got stuck in the line for about an hour on the reversal and ran itself out of battery.
2016-05-18 | SNM-1401-041 | SNM-1401-040 | SGM-1401-043 | D2 | 8 | 309 | 49 | pipe condition on the first run of 9 feet as well as on the reversal run of 40 feet.
2016-05-18 | SNM-1401-042 | SNM-1401-041 | SGM-1401-044 | D2 | 8 | 332 | 49 | Pipe condition on the initial run of 38 feet as well as on the reversal run of 11 feet.
2016-05-18 | SNM-1401-043 | SNM-1401-042 | SGM-1401-045 | D2 | 8 | 321 | 2 | Pipe condition on the first run of 2 feet and False start pipe condition the reversal run that went nowhere.
2016-05-18 | SNM-1401-051 | SNM-1401-039 | SGM-1401-054 | D2 | 8 | 320 | 72 | pipe condition on the first run of 11 feet as well as on the reversal run of 61 feet.
2016-05-18 | SNM-1401-052 | SNM-1401-051 | SGM-1401-055 | D2 | 8 | 329 | 4 | False start pipe condition on the first run of 1 foot as well as on the reversal of 3 feet
2016-05-18 | SNM-1401-053 | SNM-1401-041 | SGM-1401-056 | D2 | 8 | 183 | 7 | False start pipe condition on the first run of 3 feet as well as on the reversal run of 4 feet.
2016-05-18 | SNM-1401-054 | SNM-1401-053 | SGM-1401-057 | D2 | 8 | 209 | 8 | Pipe condition on the first run of 8 feet and the reversal was nulled because of unsuported asset, pipe reduction.
2016-05-18 | SNM-1401-056 | SNM-1401-042 | SGM-1401-059 | D2 | 8 | 239 | 89 | pipe condition on the initial run of 81 feet as well as on the reversal run of 8 feet.
2016-05-18 | SNM-1401-057 | SNM-1401-056 | SGM-1401-060 | D2 | 8 | 234 | 216 | Pipe condition on the first run of 123 feetm as well as a pipe condition on the reversal run of 93 feet.
2016-05-19 | SNM-1401-059 | SNM-1304-063 | SGM-1401-062 | D2 | 8 | 336 | 244 | I got 10 feet on the initial run but didn't do the reversal because it may need traffic.
2016-05-19 | SNM-1401-060 | SNM-1401-059 | SGM-1401-063 | D2 | 8 | 326 | 68 | False start pipe condition on the first run of 9 feet and a pipe condition on the reversal run of 59 feet
2016-05-19 | SNM-1401-061 | SNM-1401-060 | SGM-1401-064 | D2 | 8 | 345 | 45 | Got a pipe condition on my first run of 45 feet and got the robot stuck in the line until the battery quit on me so I didn't get to save the mission. Obviously I didn't run it again.
2016-05-20 | SNM-1304-063 | SNM-1304-031 | SGM-1304-065 | D2 | 8 | 251 | ? | Robot got stuck in the line and got jetted, I'm not sure of the outcome of the run.
2016-05-20 | SNM-1304-063 | SNM-1304-064 | SGM-1304-066 | D2 | 8 | 224 | 217 | Pipe condition on the first run of 41 feet, Photo shows intruding tap. Will do the reversal Sunday or when possible, traffic got too heavy. Reversal run of 176 feet resulting in pipe condition done on 5/23/16
2016-05-20 | SNM-1401-063 | SNM-1304-065 | SGM-1401-067 | D2 | 8 |  | 156 | Disconnected camera of the initial run of 156 feet. Will run the reversal on Sunday or earlier in the day tomorrow. Traffic picked up too steady.
2016-05-20 | SNM-1401-064 | SNM-1401-063 | SGM-1401-068 | D2 | 8 | 330 | 35 | Pipe condition on the first run of 14 feet as well as on the reversal run of 21 feet.
2016-05-20 | SNM-1401-065 | SNM-1401-064 | SGM-1401-069 | D2 | 8 | 361 | 300 | Pipe condition on the initial run of 8 feet as well as on the reversal run of 292 feet
2016-05-20 | SNM-1401-066 | SNM-1401-065 | SGM-1401-070 | D2 | 8 | 274 | 139 | Pipe condition on the first run of 17 feet as well as on the reversal run of 122 feet.
2016-05-20 | SNM-1401-068 | SNM-1401-067 | SGM-1401-071 | D2 | 8 | 327 | 160 | Pipe condition on the first run of 160 feet but due to the pickup of traffic at the time I'll have to do the reversal on Sunday or tomorrow
2016-05-20 | SNM-1401-069 | SNM-1401-068 | SGM-1401-072 | D2 | 8 | 327 | 8 | Got a pipe condition on the initial run of 8 feet. The robot got stuck in the line on the reversal so I don't know the outcome of that run.
2016-05-20 | SNM-1401-087 | SNM-1401-071 | SGM-1401-075 | D2 | 8 | 194 | ? | Robot got stuck in the line and the battery died before I could get him free. Didn't get the outcome of the run.
2016-05-23 | SNM-1304-033 | SNM-1304-027 | SGM-1304-037 | D2 | 8 | 70 | 0 | Nulled... SNM-1304-033 Is covered and SNM-1304-027 cannot be found.
2016-05-23 | SNM-1304-034 | SNM-1304-033 | SGM-1304-038 | D2 | 8 | 86 | 0 | Both manholes are in the same backyard. One is covered by a trailer and the other is under a trampolene
2016-05-23 | SNM-1304-059 | SNM-1304-058 | SGM-1304-061 | D2 | 8 | 322 | ? | Stuck in line... Waiting to get jetted tomorrow
2016-05-23 | SNM-1304-060 | SNM-1304-059 | SGM-1304-062 | D2 | 8 | 341 | 332 | Pipe condition on initial run of 55 feet as well as on the reversal run of 277 feet
2016-05-23 | SNM-1304-061 | SNM-1304-060 | SGM-1304-063 | D2 | 8 | 298 | 274 | Pipe condition on the initial run of 199 feet as well as on the reversal run of 75 feet.
2016-05-23 | SNM-1401-058 | SNM-1304-029 | SGM-1304-067 | D2 | 8 | 381 | 4 | False start pipe condition of 2 feet on both runs
2016-05-23 | SNM-1401-078 | SNM-1304-029 | SGM-1401-090 | D2 | 8 | 112 | 0 | Nulled... Unsupported asset at SNM-1304 -029 and I can't get SNM-1401 -078 open
2016-05-08 | snm-1402-039 | snm-1402-038 | SGM-1402-040 | f1 | 8 | 298 | 242 | 240' US to PC. 2' DS to false start debris in pipe. PC.
2016-05-08 | snm-1402-040 | snm-1402-038 | SGM-1402-041 | f1 | 8 | 339 | 114 | 114' US to PC. CNL US mh for reversal.
2016-05-08 | snm-1402-041 | snm-1402-040 | SGM-1402-042 | f1 | 8 | 438 | 420 | 420' DS to max tether. 0' US CNL DS mh for reversal.
2016-05-08 | snm-1402-044 | snm-1402-043 | SGM-1402-046 | f1 | 8 | 156 | 0 | Nulled US and DS run. DS mh is capped.
2016-05-08 | snm-1402-047 | snm-1402-046 | SGM-1402-049 | f1 | 8 | 396 | 235 | 160' US got bottom pressure. 75' DS to PC.
2016-05-07 | snm-1402-052 | snm-1402-051 | SGM-1402-054 | f1 | 8 | 299 | 208 | 160' DS to PC. 48' US to PC.
2016-05-08 | snm-1402-056 | snm-1402-042 | SGM-1402-044 | f1 | 8 | 103 | 183 | 183' US to PC. cnl US MH for reversal
2016-05-10 | snm-1402-009 | snm-1402-008 | SGM-1402-008 | f2 | 8 | 57 | 0 | CNL DS MH; traffic control needed to deploy from US MH.
2016-05-11 | snm-1402-001 | snm-1303-007 | SGM-1303-008 | f2 | 8 | 148 | 0 | US mh is surcharged. CNL DS to US segment. CNL DS mh.
2016-05-11 | snm-1402-002 | snm-1402-001 | SGM-1402-001 | f2 | 8 | 81 | 5 | 5' DS to false PC. Heavy flow in segment. Nulled DS to US segment. Heavy flow in segment.
2016-05-07 | snm-1302-034 | snm-1302-033 | SGM-1302-045 | f3 | 8 | 339 | 336 | 29' US to PC. 307' DS to PC
2016-05-07 | snm-1303-037 | snm-1303-036 | SGM-1303-073 | f3 | 8 | 540 | 15 | 15' US to false PC. Under water. Nulled DS, mh full of mudd.
2016-05-06 | snm-1303-076 | snm-1303-075 | SGM-1303-069 | f3 | 8 | 330 | 324 | 220' US to PC. 104' DS to PC also
2016-05-07 | snm-1303-077 | snm-1303-036 | SGM-1303-072 | f3 | 8 | 148 | 113 | 05-06-16 113' US to PC. Nulled reversal. Debris in pipe. Pipe too small to fit into.
2016-05-06 | snm-1303-078 | snm-1303-075 | SGM-1303-067 | f3 | 8 | 335 | 214 | 100' US to PC. 114' DS to PC also.
2016-05-06 | snm-1303-091 | snm-1303-036 | SGM-1303-071 | f3 | 8 | 139 | 0 | Nulled US and DS run. Capped off inside of the pipe.
2016-05-11 | snm-1303-088 | snm-1303-011 | SGM-1303-051 | f3 | 8 | 261 | 0 | CNL US MH. Pipe opening too small to deploy in DS MH.
2016-05-11 | snm-2404-036 | snm-2404-092 | SGM-2404-022 | f3 | 8 | 150 | 54 | 54' DS to PC. CNL DS mh.
[5 empty] | TOTAL 8" PIPE LENGTH = | 19778 | FT
2016-05-10 | snm-2301-031 | snm-2301-030 | SGM-2301-036 | f2 | 10 | 263 | 4 | 2' US to false start due to heavy flow. 2' DS to roll max. bend in start of pipe may be the reason it rolled over.
2016-05-10 | snm-1303-065 | snm-1303-061 | SGM-1303-057 | f3 | 10 | 152 | 1 | 1' US to false start PC. Pipe to small to fit into US MH.
[5 empty] | TOTAL 10" PIPE LENGTH = | 415 | FT
2016-05-10 | snm-1402-007 | snm-1402-006 | SGM-1402-006 | f2 | 12 | 85 | 0 | Nulled US to DS segment. Big diameter pipe in mh. Nulled DS to US segmemt CNL mh.
2016-05-10 | snm-1402-008 | snm-1402-007 | SGM-1402-007 | f2 | 12 | 103 | 0 | CNL US or DS mh
2016-05-10 | snm-1402-010 | snm-1402-007 | SGM-1402-010 | f2 | 12 | 90 | 0 | CNL US MH; pipe larger than 12" in DS MH.
2016-05-10 | snm-1402-055 | snm-1402-010 | SGM-1402-011 | f2 | 12 | 145 | 0 | CNL US or DS mh.
2016-05-11 | snm-1402-004 | snm-1402-002 | SGM-1402-003 | f2 | 12 | 210 | 0 | CNL US to DS segment. CNL US mh. No DS to US segment in DS mh.
2016-05-11 | snm-1402-005 | snm-1402-004 | SGM-1402-004 | f2 | 12 | 416 | 67 | 67' DS to rollmax heavy flow. CNL DS mh.
2016-05-11 | snm1402-006 | snm-1402-005 | SGM-1402-005 | f2 | 12 | 268 | 17 | 17' US to false pc. Heavy flow. CNL DS mh.
[5 empty] | TOTAL 12" PIPE LENGTH = | 1317 | FT

## NW Quad (thru 5-23) 15",18",20"
MI Owosso/OHM Project
Segments with incomplete or no inspections through May 23
Northwest Quadrant (15", 18")
Line Segment | Pipe Size | Pipe Length | Pipe Material | Geospatial ID | Map Page | Issued To | Inspection Date | Inspection Footage | Deployment Number | Initial Inspection Direction | Complete (Y/N) | Comments
SNM-1401-009 to SNM-1401-008 | 15 | 291.48 | Vitrified Clay Pipe | SGM-1401-009 | C1 | CCTV | 2016-04-28 | 84 | 83-1 | D/S | Y | SA @ 84', encrustation; CNL D/S MH to do reversal
| TOTAL 15" PIPE LENGTH = | 291.48 | FT
SNM-1401-011 to SNM-1401-010 | 18 | 180.41 | Vitrified Clay Pipe | SGM-1401-011 | C1 | CCTV | 2016-04-20 | 196 | 1-2 | D/S | Y | SA @ 149', encrustation; reversed on 84-2 for 47', complete
SNM-1401-007 to SNM-1401-006 | 18 | 250.04 | Vitrified Clay Pipe | SGM-1401-007 | C2 | CCTV | 2016-04-20 | 16 | 2-1 | U/S | Y | SA @ 16', roots; CNL 1401-007 to do reversal
SNM-1401-006 to SNM-1401-005 | 18 | 434.5 | Vitrified Clay Pipe | SGM-1401-006 | C2 | CCTV | 2016-04-20 | 41 | 3-1 | D/S | Y | SA @ 22', obstruction/deep sediment; reversed on 4-1 for 19', roots
SNM-1401-005 to SNM-1401-004 | 18 | 228.68 | Vitrified Clay Pipe | SGM-1401-005 | C2 | CCTV | 2016-04-20 | 253 | 5-1 | D/S | Y | SA @ 253'; reversed on 10-1 for 3', SA obstruction
SNM-1401-002 to SNM-1401-001 | 18 | 227.21 | Vitrified Clay Pipe | SGM-1401-002 | C2 | CCTV | 2016-04-21 | 17 | 6-2 | U/S |  | SA @ 17', roots/encrustation; reversed on 39-2 for 176', complete
SNM-1401-004 to SNM-1401-003 | 18 | 269.29 | Vitrified Clay Pipe | SGM-1401-004 | C2 | CCTV | 2016-04-21 | 222 | 11-1 | D/S | Y | SA @ 222', encrustation; reversed on 37-1 for 56', complete
SNM-1401-008 to SNM-1401-007 | 18 | 159.25 | Vitrified Clay Pipe | SGM-1401-008 | C2 | CCTV | 2016-04-21 |  |  |  |  | CNL either MH
SNM-1304-027 to SNM-1304-026 | 18 | 307.24 | Vitrified Clay Pipe | SGM-1304-031 | D2 | CCTV | 2016-04-21 | 8 | 7-3 | D/S | Y | SA @ 8', obstruction; CNL 1304-026 to do reversal
SNM-1304-026 to SNM-1304-025 | 18 | 288.81 | Vitrified Clay Pipe | SGM-1304-030 | D2 | CCTV | 2016-04-21 | 78 | 8-1 | U/S | Y | SA @ 78', rootball; CNL 1304-026 to do reversal
SNM-1401-078 to SNM-1401-001 | 18 | 92.98 | Vitrified Clay Pipe | SGM-1401-082 | D2 | CCTV | [5 empty] | CNO U/S; CNL D/S
SNM-1304-025 to SNM-1304-007 | 18 | 413.55 | Vitrified Clay Pipe | SGM-1304-029 | D3 | CCTV | 2016-04-21 | 98 | 9-1 | D/S | Y | SA @ 98', deep sediment; no access 1304-007 (far into back yard, very wet) to do reversal
| TOTAL 18" PIPE LENGTH = | 2851.96 | FT

## NE Quad (thru 5-23) 8",10",12"
MI Owosso/OHM Project
Segments with incomplete or no inspections through May 23
Northeast Quadrant (8", 10", 12")
Date | U/S MH | D/S MH | Segment ID | Map Page | Pipe Size | Map Length | Inspected Length | Comments
2016-05-09 | SNM-1302-048 | SNM-1302-047 | SGM-1301-066 | E4 | 8 | 348 | 338 | 259' D/S to camera underwater and 79' U/S to roots at tap
2016-05-09 | SNM-1301-049 | SNM-1301-048 | SGM-1301-054 | E4 | 8 | 191 | 20 | 20' U/S to roots at tap and nulled D/S drop connection
2016-05-10 | SNM-1301-054 | SNM-1301-052 | SGM-1301-059 | E4 | 8 | 358 | 267 | 77' D/S to debris and 190' U/S to heavy debris
2016-05-10 | SNM-1302-040 | SNM-1302-039 | SGM-1302-010 | E4 | 8 | 337 | 83 | 83' D/S to offset joint and nulled U/S drop connecction
2016-05-10 | SNM-1302-043 | SNM-1301-054 | SGM-1302-021 | E4 | 8 | 357 | 232 | 232' U/S to roots and too much debris for D/S reversal
2016-05-10 | SNM-1302-045 | SNM-1302-044 | SGM-1302-020 | E4 | 8 | 357 | 122 | 122' U/S to roots and nulled D/S too much debris
2016-05-11 | SNM-1302-046 | SNM-1301-056 | SGM-1301-063 | E4 | 8 | 363 | 322 | 51' D/S to debris and 271' offset joint
2016-05-11 | SNM-1302-047 | SNM-1302-046 | SGM-1302-063 | E4 | 8 | 578 | 216 | 8' D/S to broken tile and 208' U/S to calcium
2016-05-11 | SNM-1302-049 | SNM-1302-048 | SGM-1302-066 | E4 | 8 | 313 | 236 | 119' U/S to debris and 117' D/S to roots
2016-05-11 | SNM-1302-055 | SNM-1302-054 | SGM-1302-041 | E4 | 8 | 332 | 60 | 60' D/S to protruding tap and nulled U/S heavy debris.
2016-05-12 | SNM-1302-052 | SNM-1301-059 | SGM-1301-069 | E4 | 8 | 314 | 246 | 241' D/S to debris and 5' U/S to heavy debris
2016-05-12 | SNM-1302-053 | SNM-1302-052 | SGM-1302-069 | E4 | 8 | 353 | 183 | 162' U/S to roots and 21' D/S to roots
2016-05-12 | SNM-1302-057 | SNM-1302-055 | SGM-1302-042 | E4 | 8 | 232 | 19 | 19' D/S to heavy debris and U/S is a drop connection
2016-05-13 | SNM-1803-028 | SNM-1803-027 | SGM-1803-079 | E4 | 8 | 392 | 116 | 99' U/S to debris and 17' D/S to debris
2016-05-13 | SNM-1803-029 | SNM-1803-028 | SGM-1803-080 | E4 | 8 | 338 | 28 | 28' U/S to debris and nulled D/S too much debris
2016-05-13 | SNM-1803-031 | SNM-1803-030 | SGM-1803-082 | E4 | 8 | 411 | 318 | 314' U/S to roots and 4' D/S to roots
2016-05-12 | SNM-1301-060 | SNM-1804-082 | SGM-1301-070 | E5 | 8 | 528 | 299 | 282' D/S to debris and 17' U/S to debris
2016-05-12 | SNM-1804-088 | SNM-1804-115 | SGM-1804-095 | E5 | 8 | 396 | 84 | 75' U/S to debris and 9' D/S to debris
2016-05-13 | SNM-1803-034 | SNM-1803-033 | SGM-1803-046 | E5 | 8 | 226 | 155 | 134' U/S to offset joint and 21' D/S to calcium
2016-05-13 | SNM-1804-086 | SNM-1804-019 | SGM-1804-094 | E5 | 8 | 339 | 119 | 38' D/S to debris and 81' U/S to debris
2016-05-14 | SNM-1803-040 | SNM-1803-039 | SGM-1803-031 | E5 | 8 | 252 | 205 | 13' U/S to roots and 192' D/S to roots
2016-05-14 | SNM-1803-042 | SNM-1803-041 | SGM-1803-034 | E5 | 8 | 302 | 51 | 51' U/S to roots and nulled D/S surcharged
2016-05-15 | SNM-1803-044 | SNM-1803-043 | SGM-1803-037 | E5 | 8 | 313 | 133 | 133' U/S to roots and nulled D/S too much debris
2016-05-15 | SNM-1803-050 | SNM-1803-049 | SGM-1803-027 | E5 | 8 | 262 | 0 | Nulled U/S roots and nulled D/S surcharged
2016-05-15 | SNM-1803-055 | SNM-1803-011 | SGM-1803-072 | E5 | 8 | 222 | 202 | 47' D/S to camera uderwater and 155' U/S to roots
2016-05-15 | SNM-1803-070 | SNM-1803-009 | SGM-1803-012 | E5 | 8 | 334 | 118 | 118' D/S to camera underwater and nulled U/S surcharged
2016-05-15 | SNM-1804-092 | SNM-1804-019 | SGM-1804-100 | E5 | 8 | 324 | 160 | 160' D/S to debris and nulled U/S drop connection
2016-05-15 | SNM-1804-093 | SNM-1804-092 | SGM-1804-101 | E5 | 8 | 280 | 84 | 2' U/S to debris and 82' D/S to offset joint
2016-05-03 | SNM-1302-062 | SNM-1302-009 | SGM-1302-023 | F4 | 8 | 275 | 17 | 17' U/S to underwater and nulled DS due to drain plug
2016-05-05 | SNM-1803-004 | SNM-1803-003 | SGM-1803-023 | F5 | 8 | 472 | 51 | 46' U/S to off set joint and 5' D/S to debris
2016-05-07 | SNM-1803-053 | SNM-1803-009 | SGM-1803-067 | F5 | 8 | 282 | 125 | 125' U/S to roots and nulled D/S due to cleanout.
2016-05-05 | SNM-1803-057 | SNM-1803-003 | SGM-1803-007 | F5 | 8 | 440 | 222 | Full of debris
2016-05-05 | SNM-1803-058 | SNM-1803-003 | SGM-1803-008 | F5 | 8 | 328 | 71 | 48' U/S to debris and 23' D/S to debris
2016-05-06 | SNM-1803-069 | SNM-1803-068 | SGM-1803-011 | F5 | 8 | 288 | 207 | 134' U/S to roots and 73' D/S to camera underwater
2016-05-06 | SNM-1803-072 | SNM-1803-071 | SGM-1803-018 | F5 | 8 | 33 | 12 | 10' U/S to offset joint and 2' D/S to heavy debris
2016-05-08 | SNM-1803-076 | SNM-1803-083 | SGM-1803-005 | F5 | 8 | 227 | 242 | Map was off. Went 242' U/S to debris and D/S reversal has too much debris.
2016-05-08 | SNM-1803-077 | SNM-1803-022 | SGM-1803-053 | F5 | 8 | 219 | 0 | Too much debris line needs cleaned
[5 empty] | TOTAL 8" PIPE LENGTH = | 11916 | FT
2016-05-11 | SNM-1302-013 | SNM-1302-012 | SGM-1302-031 | E4 | 10 | 409 | 0 | Nulled D/S too much debris and nulled U/S drop connection
2016-05-13 | SNM-1302-054 | SNM-1302-021 | SGM-1302-040 | E5 | 10 | 397 | 0 | Needs cleaned too much debris
2016-04-22 | SNM-1302-021 | SNM-1302-020 | SGM-1302-039 | F4 | 10 | 460 | 324 | 261' D/S to calcium and 63' U/S to debris
2016-04-22 | SNM-1302-037 | SNM-1302-001 | SGM-1302-006 | F4 | 10 | 349 | 74 | Full of debris
2016-05-03 | SNM-1302-010 | SNM-1302-008 | SGM-1302-024 | F4 | 10 | 348 | 142 | 99' D/S to debris and 43' U/S to debris
2016-05-03 | SNM-1302-011 | SNM-1302-010 | SGM-1302-029 | F4 | 10 | ? | 237 | 218' D/S to debris and 19' U/S to debris
2016-05-04 | SNM-1803-015 | SNM-1803-014 | SGM-1803-075 | F4 | 10 | 342 | 318 | 16' U/S to debris and 302' D/S to debris
2016-05-05 | SNM-1803-011 | SNM-1803-010 | SGM-1803-070 | F5 | 10 | 474 | 129 | 97' D/S to roots and 32' U/S to debris
[5 empty] | TOTAL 10" PIPE LENGTH = | 2779 | FT
2016-05-13 | SNM-1803-005 | SNM-1803-004 | SGM-1803-024 | E5 | 12 | 380 | 2 | 2' U/S to debris and nulled D/S too much debris
2016-05-13 | SNM-1803-006 | SNM-1803-005 | SGM-1803-042 | E5 | 12 | 364 | 113 | 113' D/S to debris and nulled U/S too much debris
2016-05-13 | SNM-1803-007 | SNM-1803-006 | SGM-1803-043 | E5 | 12 | 363 | 199 | 59' D/S to debris and 140' U/S to debris
2016-05-13 | SNM-1803-008 | SNM-1803-007 | SGM-1803-047 | E5 | 12 | 367 | 61 | 61' U/S to debris and nulled D/S too much debris
2016-05-05 | SNM-1803-003 | SNM-1803-002 | SGM-1803-006 | F5 | 12 | 352 | 53 | 52' D/S to debris and 1' U/S to offset joint
[5 empty] | TOTAL 12" PIPE LENGTH = | 1826 | FT

## NE Quad (thru 5-23) 15",18",20"
MI Owosso/OHM Project
Segments with incomplete or no inspections through May 23
Northeast Quadrant (15", 18", 20")
Line Segment | Pipe Size | Pipe Length | Pipe Material | Geospatial ID | Map Page | Issued To | Inspection Date | Inspection Footage | Deployment Number | Initial Inspection Direction | Complete (Y/N) | Comments
SNM-1804-006 to SNM-1804-005 | 15 | 274.9 | Vitrified Clay Pipe | SGM-1804-006 | D5 | CCTV | 2016-04-22 | 167 | 12-1 | D/S |  | SA @ 5', deep sediment; reversed on 13-1 for 162', SA deep sediment
| TOTAL 15" PIPE LENGTH = | 274.9 | FT
SNM-1804-004 to SNM-1804-003 | 18 | 275.7 | Vitrified Clay Pipe | SGM-1804-004 | D5 | CCTV | 2016-04-22 | 279 | 14-1 | D/S |  | SA @ 88', obstruction; reversed on 17-1 for 189', complete
SNM-1804-003 to SNM-1804-002 | 18 | 292 |  |  | D5 | CCTV | 2016-04-22 | 292 | 19-1 | D/S | Y | SA @ 202', deep sediment; reversed on 21-1 for 90', complete
SNM-1302-002 to SNM-2401-021 | 18 | 347.75 | Vitrified Clay Pipe | SGM-1302-002 | F4 | CCTV | [5 empty] | Traffic control needed to inspect
SNM-1302-003 to SNM-1302-002 | 18 | 338.92 | Vitrified Clay Pipe | SGM-1302-003 | F4 | CCTV | [5 empty] | Traffic control needed to inspect
SNM-1302-004 to SNM-1302-003 | 18 | 336.1 | Vitrified Clay Pipe | SGM-1302-004 | F4 | CCTV | [5 empty] | Traffic control needed to inspect
SNM-1302-064 to SNM-2401-002 | 18 | 283.74 | Vitrified Clay Pipe | SGM-2401-003 | F4 | CCTV | [5 empty] | Traffic control needed to inspect
SNM-1803-013 to SNM-1302-004 | 18 | 325.17 | Vitrified Clay Pipe | SGM-1302-005 | F4 | CCTV | [5 empty] | Traffic control needed to inspect
SNM-2401-002 to SNM-2401-001 | 18 | 222.23 | Vitrified Clay Pipe | SGM-2401-002 | F4 | CCTV | [5 empty] | Traffic control needed to inspect
SNM-2401-021 to SNM-2401-020 | 18 | 330.55 | Vitrified Clay Pipe | SGM-2401-006 | F4 | CCTV | [5 empty] | Traffic control needed to inspect
| TOTAL 18" PIPE LENGTH = | 2752.16 | FT
SNM-1301-010 to SNM-1301-009 | 20 | 314.05 | Vitrified Clay Pipe | SGM-1301-010 | D4 | CCTV | 2016-04-23 | 325 | 29-2 | D/S |  | SA @ 72', rootball; reversed on 31-1 for 253', complete
SNM-1301-008 to SNM-1301-007 | 20 | 111.23 | Vitrified Clay Pipe | SGM-1301-008 | D4 | CCTV | 2016-04-23 | 107 | 33-2 | D/S | Y | SA @ 76', lost traction; reversed on 35-1 for 31', complete
| TOTAL 20" PIPE LENGTH = | 425.28 | FT

## SE Quad (thru 5-23) 8",10",12"
MI Owosso/OHM Project
Segments with incomplete or no inspections through May 23
Southeast Quadrant (8", 10", 12")
Date | U/S MH | D/S MH | Segment ID | Map Page | Pipe Size | Map Length | Inspected Length | Comments
2016-04-20 | SNM-2401-035 | SNM-2401-034 | SGM-2401-044 | G4 | 8 | 348 | 3 | 3' D/S to debris and nulled U/S drop connection
2016-04-20 | SNM-2401-038 | SNM-2401-037 | SGM-2401-047 | G4 | 8 | 329 | 209 | 209' U/S to debris and nulled D/S CNL
2016-04-19 | SNM-2401-049 | SNM-2401-025 | SGM-2401-062 | G4 | 8 | 331 | 345 | 345' U/S to heavy debris and nulled D/S heavy debris
2016-04-20 | SNM-2401-062 | SNM-2401-060 | SGM-2401-073 | G4 | 8 | 289 | 4 | 4' U/S to debris and nulled D/S surcharged
2016-04-22 | SNM-2401-064 | SNM-2401-063 | SGM-2401-079 | G4 | 8 | 173 | 0 | Full of debris
2016-04-22 | SNM-2401-065 | SNM-2401-064 | SGM-2401-080 | G4 | 8 | 185 | 0 | Full of debris
2016-04-17 | SNM-1904-038 | SNM-1904-008 | SGM-1904-035 | G5 | 8 | 405 | 345 | 345' U/S to roots and nulled D/S too much debris
2016-04-16 | SNM-2401-031 | SNM-2401-030 | SGM-2401-033 | H4 | 8 | 344 | 277 | 277' U/S to debris and nulled D/S too much debris
2016-04-15 | SNM-2401-072 | SNM-2401-029 | SGM-2401-031 | H4 | 8 | 223 | 205 | 205' U/S to debris and nulled D/S too much debris.
2016-04-16 | SNM-2401-074 | SNM-2401-073 | SGM-2401-035 | H4 | 8 | 265 | 232 | 232' U/S to debris and nulled D/S too much debris
2016-04-14 | SNM-2402-025 | SNM-2402-024 | SGM-2402-054 | H4 | 8 | 240 | 19 | 19' D/S to protruding tap and nulled U/S too much debris
2016-04-14 | SNM-2402-026 | SNM-2402-025 | SGM-2402-055 | H4 | 8 | 124 | 55 | 55' U/S to roots and nulled D/S too much debris
2016-04-14 | SNM-2402-027 | SNM-2402-024 | SGM-2402-021 | H4 | 8 | 378 | 210 | 5' D/S to debris and 205' U/S to debris
2016-04-14 | SNM-2402-028 | SNM-2402-027 | SGM-2402-022 | H4 | 8 | 435 | 1 | 1' U/S to debris and nulled D/S too much debris
2016-04-14 | SNM-2402-029 | SNM-2402-028 | SGM-2402-023 | H4 | 8 | 334 | 35 | 35' D/S to debris and nulled U/S too much debris
2016-04-14 | SNM-2402-033 | SNM-2402-032 | SGM-2402-028 | H4 | 8 | 340 | 22 | 18' D/S to roots and 4' U/S to heavy debris
2016-04-14 | SNM-2402-034 | SNM-2402-033 | SGM-2402-029 | H4 | 8 | 377 | 36 | 36' U/S to roots and nulled D/S too much debris
2016-04-15 | SNM-2402-040 | SNM-2402-004 | SGM-2402-016 | H4 | 8 | 237 | 59 | 39' D/S to grease and 20' U/S to debris
2016-04-15 | SNM-2402-044 | SNM-2402-002 | SGM-2402-012 | H4 | 8 | 478 | 368 | 368' D/S to debris and nulled U/S surcharged
2016-04-15 | SNM-2402-048 | SNM-2402-001 | SGM-2402-007 | H4 | 8 | 343 | 84 | 16' D/S to debris and 68' U/S to debris
2016-04-18 | SNM-2401-084 | SNM-2401-077 | SGM-2401-040 | H4 | 8 | 412 | 0 | Nulled both ways. Too much debris. Needs cleaned clear to street.
2016-04-12 | SNM-1903-009 | SNM-1904-019 | SGM-1904-056 | H5 | 8 | 291 | 174 | 174' D/S to calcium and nulled U/S to drop connection
2016-04-12 | SNM-1903-010 | SNM-1903-009 | SGM-1903-063 | H5 | 8 | 289 | 61 | 52' U/S to broken pipe and 9' D/S to broken pipe
2016-04-12 | SNM-1903-012 | SNM-1904-020 | SGM-1903-012 | H5 | 8 | 447 | 338 | 338' D/S to heavy debris and nulled U/S surcharged
2016-04-12 | SNM-1904-041 | SNM-1904-040 | SGM-1904-049 | H5 | 8 | 241 | 7 | 7' U/S to debris and nulled D/S solid pipe through MH
2016-04-12 | SNM-1904-042 | SNM-1904-041 | SGM-1904-050 | H5 | 8 | 243 | 89 | 89' D/S to debris and nulled U/S solid pipe through MH
2016-04-12 | SNM-1904-045 | SNM-1904-042 | SGM-1904-051 | H5 | 8 | 141 | 94 | 92' U/S to roots and 2' D/S to roots
2016-04-12 | SNM-1904-046 | SNM-1904-016 | SGM-1904-042 | H5 | 8 | 233 | 14 | 14' D/S to roots and nulled U/S traffic control
2016-04-12 | SNM-1904-049 | SNM-1904-022 | SGM-1904-045 | H5 | 8 | 365 | 20 | 20' D/S to calcium and nulled U/S traffic control
2016-04-13 | SNM-1901-001 | SNM-1901-002 | SGM-1901-001 | H6 | 8 | 349 | 256 | 204' D/S to debris and 52' U/S to calcium
2016-04-13 | SNM-1901-003 | SNM-1901-004 | SGM-1901-004 | H6 | 8 | 319 | 290 | 290' D/S to roots and nulled U/S drop connection
2016-04-13 | SNM-1901-004 | SNM-1901-013 | SGM-1901-003 | H6 | 8 | 263 | 1 | 1' D/S to debris and nulled U/S too much debris
2016-04-13 | SNM-1901-005 | SNM-1901-004 | SGM-1901-005 | H6 | 8 | 129 | 28 | 28' D/S to debris and nulled U/S drop connection
2016-04-12 | SNM-1901-008 | SNM-1901-010 | SGM-1901-010 | H6 | 8 | 296 | 0 | Nulled heavy debris
2016-04-12 | SNM-1901-008 | SNM-1901-007 | SGM-1901-008 | H6 | 8 | 198 | 0 | Nulled D/S channel too narrow and Nulled U/S too much debris
2016-04-12 | SNM-1901-009 | SNM-1901-008 | SGM-1901-009 | H6 | 8 | 156 | 0 | Nulled D/S CNL U/S MH and nulled U/S channel too narrow
2016-04-13 | SNM-1901-012 | SNM-1902-019 | SGM-1902-011 | H6 | 8 | 267 | 74 | 74' U/S to calcium and nulled D/S due to drop connection
2016-04-13 | SNM-1902-014 | SNM-1902-001 | SGM-1902-002 | H6 | 8 | 301 | 18 | 18' D/S to roots and nulled U/S traffic control
2016-04-13 | SNM-1902-019 | SNM-1902-004 | SGM-1903-019 | H6 | 8 | 279 | 64 | 64' D/S to calcium and nulled U/S due traffic control
2016-04-13 | SNM-1902-023 | SNM-1902-022 | SGM-1902-017 | H6 | 8 | 32 | 0 | Needs cleaned too much debris
2016-03-26 | SNM-2402-043 | SNM-2402-042 |  | I4 | 8 | 462 | 36 | 29' U/S to debris and 7' D/S to debris
2016-03-26 | SNM-2402-047 | SNM-2402-046 |  | I4 | 8 | 291 | 84 | 30' U/S to service line and 54' D/S to debris
2016-03-26 | SNM-2402-050 | SNM-2402-049 |  | I4 | 8 | 297 | 36 | 36' D/S to debris and nulled U/S CNL 049
2016-03-26 | SNM-2402-049 | SNM-2402-048 |  | I4 | 8 | 351 | 14 | 14' U/S to debris and Nulled D/S to CNL
2016-03-26 | SNM-2402-053 | SNM-2402-053 |  | I4 | 8 | 360 | 282 | 278' D/S to debris and 4' U/S to calcium
2016-03-30 | SNM-2402-037 | SNM-2402-036 |  | I4 | 8 | 411 | 350 | 350' U/S to debris and nulled D/S too much debris
2016-03-30 | SNM-2402-036 | SNM-2402-035 |  | I4 | 8 | 342 | 105 | 39' D/S to debris and 66' U/S to roots
2016-03-30 | SNM-2402-010 | SNM-2402-009 |  | I4 | 8 | 58 | 18 | 18' U/S to debris and nulled D/S too much debris
2016-04-01 | SNM-2402-030 | SNM-2402-029 |  | I4 | 8 | 350 | 123 | 13' D/S to debris and 110' U/S to debris
2016-04-02 | SNM-1902-027 | SNM-1902-026 |  | I6 | 8 | 347 | 251 | 251' D/S to debris and nulled U/S narrow channel
2016-04-02 | SNM-1902-026 | SNM-1902-011 |  | I6 | 8 | 400 | 35 | 35' U/S to debris and nulled D/S channel too narrow
2016-04-02 | SNM-1902-011 | SNM-1902-010 |  | I6 | 8 | 371 | 263 | 248' D/S to debris and 15' U/S to debris
2016-04-02 | SNM-1902-009 | SNM-1903-006 |  | I6 | 8 | 291 | 115 | 59' D/S to debris and 56' U/S to debris
2016-04-11 | SNM-1902-021 | SNM-1902-020 | SGM-1902-014 | I6 | 8 | 307 | 92 | 61' U/S to debris and 31' D/S to calcium
2016-04-11 | SNM-1902-025 | SNM-1902-024 | SGM-1902-021 | I6 | 8 | 292 | 17 | 17' U/S to heavy debris and nulled D/S CNL
2016-04-11 | SNM-1903-005 | SNM-1903-004 | SGM-1903-005 | I6 | 8 | 362 | 349 | 349' D/S to debris and nulled U/S too much debris
2016-03-23 | SNM-1903-061 | SNM-1903-060 |  | J5 | 8 | 187 | 120 | 2' D/S to calcium and 118' camera went underwater
2016-03-23 | SNM-1903-018 | SNM-1903-017 |  | J5 | 8 | 350 | 172 | 4' D/S to roots at tap and 168' U/S to debris
2016-03-23 | SNM-1903-028 | SNM-1903-026 |  | J5 | 8 | 335 | 113 | 69' U/S to off set joint and 44' D/S to Rm on debris
2016-03-24 | SNM-1903-035 | SNM-1903-034 |  | J5 | 8 | 155 | 1 | 1' U/S to incline, robot kept sliding down and Nulled D/S due to cleanout U/S
2016-03-24 | SNM-1903-042 | SNM-1903-041 |  | J5 | 8 | 332 | 282 | 16' D/S to camera uderwater and 266' U/S to roots
2016-03-25 | SNM-1903-049 | SNM-1903-048 |  | J5 | 8 | 77 | 1 | 1' D/S to rootball and nulled U/S roots
2016-03-25 | SNM-1903-048 | SNM-1903-047 |  | J5 | 8 | 262 | 8 | 1' D/S to rootball and 7' U/S rootball
2016-03-25 | SNM-1903-054 | SNM-1903-053 |  | J5 | 8 | 324 | 240 | 240' D/S to debris and nulled U/S debris
2016-03-25 | SNM-1903-043 | SNM-1903-042 |  | J5 | 8 | 120 | 0 | Nulled D/S CNL U/S MH and nulled U/S roots
2016-03-21 | SNM-3001-004 | SNM-3001-001 |  | J6 | 8 | 59 | 0 | D/S MH is a drop and U/S MH robot wouldn’t fit in channel
2016-03-21 | SNM-3001-003 | SNM-3001-002 |  | J6 | 8 | 599 | 182 | 182' D/S to roots and Nulled U/S drop connection
2016-03-22 | SNM-3001-010 | SNM-3001-009 |  | J6 | 8 | 143 | 140 | 140' D/S to debris and nulled U/S due to debris
2016-03-22 | SNM-3001-012 | SNM-3001-011 |  | J6 | 8 | 372 | 0 | CNL D/S MH and U/S has debris
2016-03-22 | SNM-3001-013 | SNM-3001-012 |  | J6 | 8 | 168 | 0 | CNL U/S MH and D/S has a drop connection
[5 empty] | TOTAL 8" PIPE LENGTH = | 20204 | ft
2016-04-18 | SNM-1904-010 | SNM-1904-009 | SGM-1904-011 | G5 | 10 | 241 | 115 | 101' U/S to debris and 14' D/S to debris
2016-04-18 | SNM-1904-011 | SNM-1904-010 | SGM-1904-012 | G5 | 10 | 324 | 34 | 4' D/S to debris and 30' U/S to debris
[5 empty] | TOTAL 10" PIPE LENGTH = | 565 | ft
2016-04-17 | SNM-1904-007 | SNM-1904-006 | SGM-1904-007 | G5 | 12 | 330 | 187 | 104' D/S to roots and 83 U/S to debris
2016-04-16 | SNM-1903-001 | SNM-1904-020 | SGM-1903-001 | H5 | 12 | 408 | 153 | 153' D/S debris and nulled U/S too much debris
2016-04-16 | SNM-1903-002 | SNM-1903-001 | SGM-1903-002 | H5 | 12 | 354 | 14 | 2' U/S to debris and 12' D/S to debris
2016-04-16 | SNM-1904-020 | SNM-1904-019 | SGM-1904-057 | H5 | 12 | 328 | 156 | 156' U/S to debris and nulled D/S too much debris
[5 empty] | TOTAL 12" PIPE LENGTH = | 1420 | ft

## SE Quad (thru 5-23) 15",18",20"
MI Owosso/OHM Project
Segments with incomplete or no inspections through May 23
Southeast Quadrant (15", 18", 20")
Line Segment | Pipe Size | Pipe Length | Pipe Material | Geospatial ID | Map Page | Issued To | Inspection Date | Inspection Footage | Deployment Number | Initial Inspection Direction | Complete (Y/N) | Comments
SNM-1904-005 to SNM-1904-005A | 15 | 318.58 | Vitrified Clay Pipe | SGM-1904-005 | G5 | CCTV | 2016-04-24 | 288 | 41-1 | D/S | Y | SA @ 20', large rock; reversed 4/24/16 on 43-1 for 268', complete.
SNM-2402-005 to SNM-2402-004 | 15 | 339.78 | Vitrified Clay Pipe | SGM-2402-004 | H4 | CCTV | 2016-04-27 | 332 | 78-1 | U/S |  | SA @ 239', encrustation; reversed on 82-1 for 93', complete
SNM-2402-003 to SNM-2402-002 | 15 | 181.91 | Vitrified Clay Pipe | SGM-2402-002 | H4 | CCTV | 2016-04-27 | 13 | 79-2 | D/S | Y | SA @ 13', encrustation; no reversal, D/S MH surcharged
SNM-2402-002 to SNM-2402-001 | 15 | 283.3 | Vitrified Clay Pipe | SGM-2402-001 | H4 | CCTV | 2016-04-27 | 230 | 80-1 | U/S | Y | 20" per field crew. SA @ 230', water level too high; no reversal, U/S MH surcharged
| TOTAL 15" PIPE LENGTH = | 1123.57 | FT
SNM-1904-004 to SNM-1904-003 | 18 | 395.66 | Vitrified Clay Pipe | SGM-1904-004 | G5 | CCTV | 2016-04-24 | 4 | 47-1 | U/S | Y | SA @ 4', obstruction; CNL 1904-004 to do reversal
SNM-1904-003 to SNM-1904-002 | 18 | 329.41 | Vitrified Clay Pipe | SGM-1904-003 | G5 | CCTV | 2016-04-24 | 333 | 49-1 | D/S | Y | SA @ 67', obstruction; reversed on 51-1 for 266', complete
| TOTAL 18" PIPE LENGTH = | 725.07 | FT
SNM-2401-024 to SNM-2401-023 | 20 | 242.71 | Vitrified Clay Pipe | SGM-2401-025 | G4 | CCTV | 2016-04-24 | 13 | 57-1 | D/S | Y | SA @ 13', deep sediment; reversed on 59-1 for 0', deep sediment
SNM-2401-023 to SNM-2401-022 | 20 | 269.81 | Vitrified Clay Pipe | SGM-2401-024 | G4 | CCTV | 2016-04-25 | 0 | 61-1 | D/S | Y | SA @ 0', deep sediment; reversed on 63-1 for 0', deep sediment
SNM-1904-001 to SNM-2401-024 | 20 | 643.65 | Vitrified Clay Pipe | SGM-1904-001 | G5 | CCTV | 2016-04-24 | 56 | 53-2 | D/S | Y | SA @ 56', obstruction; reversed on 55-1 for 17', SA deep sediment
SNM-2402-001 to SNM-2401-019 | 20 | 389.56 | Vitrified Clay Pipe | SGM-2401-022 | H4 | CCTV | 2016-04-27 | 131 | 81-1 | D/S |  | SA @ 131', deep sediment; awaiting reversal
| TOTAL 20" PIPE LENGTH = | 1545.73 | FT

## SW Quad (thru 5-23) 15",18",20"
MI Owosso/OHM Project
Segments with incomplete or no inspections through May 23
Southwest Quadrant (15", 18", 20")
Line Segment | Pipe Size | Pipe Length | Pipe Material | Geospatial ID | Map Page | Issued To | Inspection Date | Inspection Footage | Deployment Number | Initial Inspection Direction | Complete (Y/N) | Comments
SNM-2302-006 to SNM-2302-005 | 18 | 365.5 | Vitrified Clay Pipe | SGM-2302-006 | I2 | CCTV | 2016-04-25 | 3 | 65-1 | D/S | Y | SA @ 3', deep sediment; reversed on 66-1 for 3', SA deep sediment
SNM-2302-005 to SNM-2302-068 | 18 | 175.8 | Vitrified Clay Pipe | SGM-2302-005 | I2 | CCTV | 2016-04-27 | 0 | 67-1 | D/S | Y | SA @ 0', deep sediment; reversed on 68-1 for 0', SA deep sediment
SNM-2302-068 to SNM-2403-005 | 18 | 193.7 | Vitrified Clay Pipe | SGM-2302-004 | I2 | CCTV | 2016-04-27 | 0 | 69-1 | D/S | Y | SA @ 0', deep sediment; too much debris in D/S MH to do reversal
SNM-2403-005 to SNM-2403-003 | 18 | 176.66 | Vitrified Clay Pipe | SGM-2403-041 | I2 | CCTV | 2016-04-27 | 2 | 70-1 | U/S |  | SA @ 2', deep sediment; too much debris in U/S MH to do reversal
SNM-2403-003 to SNM-2302-003 | 18 | 149.04 | Vitrified Clay Pipe | SGM-2403-040 | I2 | CCTV | 2016-04-27 | 6 | 71-1 | D/S |  | SA @ 6', deep sediment; reversed on 72-1 for 0', SA deep sediment
SNM-2302-003 to SNM-2302-002 | 18 | 265.32 | Vitrified Clay Pipe | SGM-2302-003 | I2 | CCTV | 2016-04-27 | 3 | 73-1 | D/S |  | SA @ 3', deep sediment; no reversal due to 2302-002 being surcharged
| TOTAL 18" PIPE LENGTH = | 1326.02 | FT